## 表2-2 Fixtures
ID (app key) | Fixture (器具名) | Spec / Faucet (水栓・仕様) | Max Flow [L/min] | Min Pres. [kPa] | FU Public (公共) | FU Private (私室) | Conn Dia [mm] | Flush Type (valve/tank/none) | Notes
wc_valve | Toilet (大便器) | Flush Valve - Type I (洗浄弁 I型 ≤8.5L) | 100 | 70 | 8 | 6 | 25 | valve
wc_valve2 | Toilet (大便器) | Flush Valve - Type II (洗浄弁 II型 ≤6.5L) | 100 | 70 | 6 | 6 | 25 | valve
wc_tank | Toilet (大便器) | Flush Tank - Type I (洗浄タンク I型 ≤8.5L) | 10 | 50 | 4 | 3 | 13 | tank
wc_tank2 | Toilet (大便器) | Flush Tank - Type II (洗浄タンク II型 ≤6.5L) | 10 | 50 | 3 | 3 | 13 | tank
wc_spec | Toilet (大便器) | Special Flush Valve (専用洗浄弁 5.5–6.5L) | 10 | 50 | 4 | 4 | 13 | valve
wc_spec2 | Toilet (大便器) | Special Flush Valve (専用洗浄弁 ≤5.5L) | 20 | 70 | 3 | 3 | 13 | valve
bidet | Bidet (温水洗浄便座) | Standard (標準) | 2 | 60 | 1 | 1 | 13 | none
urinal | Urinal (小便器) | Flush Valve (洗浄弁 2–4L) | 15 | 70 | 3 | 2 | 13 | valve
urinal_spec | Urinal (小便器) | Special Flush Valve (専用洗浄弁 2–4L) | 15 | 70 | 3 | 2 | 13 | valve
handwash | Hand Wash (手洗器) | Manual/Auto (手動・自動水栓) | 8 | 30 | 1 | 0.5 | 13 | none
washbasin | Wash Basin (洗面器) | Manual/Auto (手動・自動水栓) | 10 | 30 | 2 | 1 | 13 | none
medical_sink | Medical Basin (医療) | Special Flush Valve (専用洗浄弁) | 10 | 30 | 3 | 1 | 13 | none
office_sink | Office Sink (事務室) | Special Flush Valve (専用洗浄弁) | 12 | 30 | 3 | 1 | 13 | none
kitchen | Kitchen Sink (台所) | Special Flush Valve (専用洗浄弁) | 12 | 30 | 2 | 3 | 13 | none
cooking_sup | Cooking Sink (料理場) | Supply Faucet (給水栓) | 15 | 30 | 4 | 2 | 20 | none
cooking_mix | Cooking Sink (料理場) | Mixing Faucet (湯水混合栓) | 15 | 30 | 3 | 4 | 20 | none
dishwasher | Dishwasher Sink (食器) | Mixing Faucet (湯水混合栓) | 15 | 30 | 5 | 4 | 20 | none
combo_sink | Combo Sink (連合) | Mixing Faucet (湯水混合栓) | 15 | 30 | 3 | 3 | 20 | none
washup_sink | Wash-up Sink (洗面流) | Per Faucet (水栓一個につき) | 12 | 30 | 2 | 0.5 | 13 | none
mop | Service Sink (掃除) | Per Faucet (水栓一個につき) | 15 | 30 | 4 | 3 | 13 | none
sink13 | General Sinks (流し) | 13mm Faucet (13mm 水栓) | 15 | 30 | 2.5 | 2.5 | 13 | none
sink20 | General Sinks (流し) | 20mm Faucet (20mm 水栓) | 25 | 30 | 2.5 | 2.5 | 20 | none
drinking_f | Drinking Fountain | 20mm Faucet/Bubbler (吹上げ式) | 3 | 30 | 1 | 1 | 20 | none
drinking_tap | Drinking Faucet | Standard (水飲み水栓) | 3 | 30 | 2 | 1 | 13 | none
hose | Hose Bib (散水栓) | 13A Standard (一般 13A) | 20 | 30 | 2 | 2 | 13 | none
hose20 | Hose Bib (散水栓) | 20A Standard (一般 20A) | 25 | 30 | 3 | 3 | 20 | none
garden | Garden Hydrant (庭園) | Auto Faucet (自動水栓) | 50 | 30 | 3 | 5 | 13 | none
bathtub_j | JP Bathtub (和風) | Supply Faucet (給水栓) | 30 | 30 | 4 | 2 | 20 | none
bathtub | US Bathtub (洋風) | Supply Faucet (給水栓) | 30 | 30 | 4 | 2 | 20 | none
shower | Shower (シャワー) | Supply Faucet 13mm (給水栓) | 12 | 70 | 4 | 2 | 13 | none
shower20 | Shower (シャワー) | Supply Faucet 20mm (給水栓) | 20 | 70 | 4 | 2 | 20 | none
bath_suite_v | Bath Suite (浴室一式) | w/ Flush Valve (大便器:洗浄弁) | 100 | 70 | 8 | 6 | 25 | valve
bath_suite_t | Bath Suite (浴室一式) | w/ Flush Tank (大便器:タンク) | 20 | 50 | 6 | 6 | 13 | tank
wh_tank | Water Heater (湯沸) | Ball Tap (ボールタップ) | 10 | 30 | 2 | 2 | 13 | none
wh_s | Instant Heater (瞬間) | Size 4–5 (4–5号) | 10 | 40 | 2 | 2 | 13 | none
wh_m | Instant Heater (瞬間) | Size 7–16 (7–16号) | 15 | 50 | 2 | 2 | 15 | none
wh_l | Instant Heater (瞬間) | Size 24–32 (24–32号) | 25 | 80 | 2 | 2 | 20 | none
faucet_gen | Faucets (水栓一般) | General Faucet (一般水栓) | 15 | 30 | 2 | 2 | 13 | none
faucet_auto | Faucets (水栓一般) | Auto Faucet (自動水栓) | 10 | 60 | 2 | 2 | 13 | none
faucet_ball | Faucets (水栓一般) | Ball Tap (ボールタップ) | 10 | 30 | 2 | 2 | 13 | none
注: * 給湯栓併用の場合は、1個の水栓に対する器具給水負荷単位は、本表の値の3/4とする。 ¦ Note: When combined with a hot water faucet, multiply FU by 3/4.