## README
配管流量線図 外部参照データ / Pipe Flow Diagram Reference Data
Formula (HW) | Q = 4.87 × C × d^2.63 × i^0.54 × 1000
Formula (TW) | poly sheet uses TW formula with C = 215
Q unit | L/min
i unit | kPa/m (pressure loss per metre)
d / id_mm | pipe inner diameter [mm]
v unit | m/s
eq_len unit | m (equivalent straight-pipe length)
Anchor points | (x1,y1)→(x2,y2) are digitised log-log endpoints of each pipe line. Interpolate with: log10(Q) = m·log10(i) + b where m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)), b=log10(y1)−m·log10(x1)
Q from i | Q = 10^( m·log10(i) + b )
i from Q | i = 10^( (log10(Q) − b) / m )
Velocity check | v = (Q/60/1000) / (π/4 × (id_mm/1000)²)
Effective id from anchor | d_eff = avg( (y1/(4870·C·x1^0.54))^(1/2.63)·1000, (y2/(4870·C·x2^0.54))^(1/2.63)·1000 )
Valid range | Only interpolate within [x1,x2]. Do NOT extrapolate beyond endpoints.
Sheets in this workbook
sgpw | 図7-2 硬質塩化ビニルライニング鋼管 C=130
vpvc | 図7-3 硬質ポリ塩化ビニル管 C=130
copper | 図7-4 銅管 C=130
sgp | 図7-5 鋼管（配管用炭素鋼鋼管） C=100
sus | 図7-6 ステンレス鋼管 C=140
hsgpw | 図7-7 耐熱性硬質塩化ビニルライニング鋼管 C=130
poly | 図7-8 ポリエチレン管 C=215 (TW式)
JSON | Full machine-readable JSON — paste into your software

## sgpw
図7-2 硬質塩化ビニルライニング鋼管流量線図
Hard PVC-lined steel pipe (JIS G 3442 SGPW)
Formula | Hazen-Williams (HW)
C | 130
DN suffix | A
i range [kPa/m] | 0.01 – 10
Q range [L/min] | 1 – 10000
A PIPE SIZES — Log-log anchor points (x=i [kPa/m], y=Q [L/min])
DN | id_mm | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2) | note
15 A | 13.263 | 0.023429 | 1 | 10 | 24.4057
20 A | 18.911 | 0.01 | 1.5994 | 10 | 62.2709
25 A | 25.128 | 0.01 | 3.2787 | 10 | 135.5285
32 A | 33.31 | 0.01 | 7.0128 | 10 | 279.0647
40 A | 39.026 | 0.01 | 10.569 | 10 | 425.9633
50 A | 50.644 | 0.01 | 20.5322 | 10 | 863.6182
65 A | 65.843 | 0.01 | 40.8699 | 10 | 1725.4212
80 A | 77.834 | 0.01 | 64.9727 | 10 | 2616.5304
100 A | 102.428 | 0.01 | 131.0725 | 10 | 5498.3146
125 A | 127.267 | 0.01 | 232 | 10 | 9733.2501
150 A | 151.92 | 0.01 | 364.7822 | 4.3325 | 10000
200 A | 201.539 | 0.01 | 765.5682 | 1.0898 | 10000
250 A | 250.625 | 0.01 | 1404.7116 | 0.4012 | 10000
300 A | 299.714 | 0.01 | 2180.454 | 0.1586 | 10000
350 A | 335.318 | 0.01 | 2934.3961 | 0.0921 | 10000
B VELOCITY REFERENCE LINES — Log-log anchor points
v [m/s] | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2)
0.2 | 0.01 | 39.5044 | 0.086747 | 1
0.3 | 0.01 | 218.5244 | 0.23132 | 1
0.4 | 0.01 | 760.6724 | 0.45981 | 1
0.6 | 0.01 | 4055.063 | 1.2277 | 1
0.8 | 0.011917 | 10000 | 2.3669 | 1
1 | 0.020604 | 10000 | 4.0924 | 1
1.5 | 0.052234 | 10000 | 10 | 1.2851
2 | 0.10703 | 10000 | 10 | 4.1145
3 | 0.29122 | 10000 | 10 | 21.9716
5 | 1.0092 | 10000 | 10 | 188.0955
C EQUIVALENT LENGTHS [m] — 局部抵抗の相当長
DN_mm | elbow_90° | elbow_45° | tee_branch | tee_straight | gate_valve | globe_valve | angle_valve | check_swing | check_shock | Y_strainer | socket
15 | *3.0 | *2.3 | *3.8 | *1.2 | *3.50 | 4.5 | 2.4 | *5.5 | — | *3.34 | *1.0
20 | *3.1 | *2.2 | *3.8 | *1.6 | *2.30 | 6 | 3.6 | *2.7 | — | *4.37 | *0.7
25 | *3.2 | *1.8 | *3.3 | *1.2 | *1.70 | 7.5 | 4.5 | *2.9 | — | *5.85 | *0.5
32 | *3.6 | *2.3 | *4.0 | *1.4 | *1.30 | 10.5 | 5.4 | *3.2 | — | *8.51 | *0.7
40 | *3.3 | *1.9 | *3.6 | *0.9 | *1.70 | 13.5 | 6.6 | *2.6 | — | *8.25 | *0.6
50 | *3.3 | *1.9 | *3.5 | *0.9 | *1.90 | 16.5 | 8.4 | *3.7 | 9.3 | *9.79 | *0.4
65 | *4.4 | *2.4 | *4.4 | *1.1 | 0.48 | 19.5 | 10.2 | 4.6 | 9.8 | 11.45 | *0.4
80 | *4.6 | *2.4 | *4.9 | *1.3 | 0.63 | 24 | 12 | 5.7 | 9 | 14.11 | *0.4
100 | 4.2 | 2.4 | 6.3 | 1.2 | 0.81 | 37.5 | 16.5 | 7.6 | 10.6 | 21.62 | —
125 | 5.1 | 3 | 7.5 | 1.5 | 0.99 | 42 | 21 | 10 | 11.9 | 31.57 | —
150 | 6 | 3.6 | 9 | 1.8 | 1.2 | 49.5 | 24 | 12 | 9.7 | 41.17 | —
200 | 6.5 | 3.7 | 14 | 4 | 1.4 | 70 | 33 | 15 | 13.3 | 54.83 | —
250 | 8 | 4.2 | 20 | 5 | 1.7 | 90 | 43 | 19 | 13.2 | 70.37 | —
Note: * = 管端防食機構付き。フート弁はアングル弁と同じ。ストレーナーはスクリーン7メッシュ程度。
Interpolation: m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)) b=log10(y1)−m·log10(x1) → Q=10^(m·log10(i)+b) ¦ i=10^((log10(Q)−b)/m)

## vpvc
図7-3 硬質ポリ塩化ビニル管流量線図
Rigid PVC pipe (JIS K 6741 VP/HIVP)
Formula | Hazen-Williams (HW)
C | 130
DN suffix
i range [kPa/m] | 0.01 – 10
Q range [L/min] | 1 – 10000
A PIPE SIZES — Log-log anchor points (x=i [kPa/m], y=Q [L/min])
DN | id_mm | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2) | note
13 | 13.785 | 0.021813 | 1 | 10 | 28.7766
16 | 16.745 | 0.01 | 1.1242 | 10 | 46.7425
20 | 20.948 | 0.01 | 2.0167 | 10 | 84.6348
25 | 25.855 | 0.01 | 3.5508 | 10 | 145.4083
30 | 31.935 | 0.01 | 6.1639 | 10 | 254.4254
40 | 40.941 | 0.01 | 11.8681 | 10 | 488.1309
50 | 52.106 | 0.01 | 22.3254 | 10 | 922.5302
65 | 68.523 | 0.01 | 44.0101 | 10 | 1975.4219
75 | 78.339 | 0.01 | 63.9425 | 10 | 2750.7281
100 | 101.074 | 0.01 | 126.6856 | 10 | 5304.1643
125 | 125.776 | 0.01 | 221.7195 | 10 | 9571.2948
150 | 148.228 | 0.01 | 340.8615 | 4.8562 | 10000
B VELOCITY REFERENCE LINES — Log-log anchor points
v [m/s] | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2)
0.2 | 0.01 | 39.1558 | 0.088642 | 1
0.3 | 0.01 | 209.8414 | 0.23604 | 1
0.4 | 0.01 | 686.0807 | 0.48225 | 1
0.5 | 0.01 | 1665.387 | 0.81157 | 1
0.6 | 0.01 | 3421.851 | 1.3007 | 1
0.8 | 0.011206 | 10000 | 2.5994 | 1
1 | 0.019441 | 10000 | 4.5758 | 1
1.5 | 0.051531 | 10000 | 10 | 1.4209
2 | 0.11234 | 10000 | 10 | 4.3592
3 | 0.29114 | 10000 | 10 | 24.968
5 | 1.0365 | 10000 | 10 | 202.8738
C EQUIVALENT LENGTHS [m] — 局部抵抗の相当長
DN_mm | elbow_90° | bend_90° | elbow_45° | tee_reducer_socket
13 | 0.5 | — | — | —
16 | 0.5 | — | — | —
20 | 0.5 | — | — | —
25 | 0.5 | — | — | —
30 | 0.8 | — | — | 1
40 | 0.8 | — | — | 1
50 | 1.2 | — | — | 1.5
75 | — | 1.5 | 0.8 | 2
100 | — | 2 | 1 | 3
125 | — | 3 | 1.5 | 5
Note: チー及び径違いソケットは設置された側の呼び径とする。チー分流は90°エルボ＋チー直流。
Interpolation: m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)) b=log10(y1)−m·log10(x1) → Q=10^(m·log10(i)+b) ¦ i=10^((log10(Q)−b)/m)

## copper
図7-4 銅管流量線図
Copper pipe (JIS H 3300 L/M type)
Formula | Hazen-Williams (HW)
C | 130
DN suffix
i range [kPa/m] | 0.01 – 10
Q range [L/min] | 1 – 10000
A PIPE SIZES — Log-log anchor points (x=i [kPa/m], y=Q [L/min])
DN | id_mm | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2) | note
10L | 11.049 | 0.061965 | 1 | 10 | 15.7956
10M | 11.59 | 0.049107 | 1 | 10 | 17.9145
15L | 14.046 | 0.01942 | 1 | 10 | 29.8363
15M | 14.664 | 0.014999 | 1 | 10 | 32.5447
20L | 19.989 | 0.01 | 1.7595 | 10 | 75.802
20M | 20.759 | 0.01 | 1.9742 | 10 | 82.4236
25L | 26.037 | 0.01 | 3.6244 | 10 | 147.8219
25M | 27.268 | 0.01 | 4.0815 | 10 | 167.3703
32M | 32.893 | 0.01 | 6.629 | 10 | 276.3314
40M | 39.116 | 0.01 | 10.5715 | 10 | 431.0667
50M | 51.382 | 0.01 | 21.504 | 10 | 889.7842
65M | 63.611 | 0.01 | 36.8398 | 10 | 1596.3719
80M | 76.079 | 0.01 | 59.7493 | 10 | 2523.8251
100M | 100.803 | 0.01 | 126.2924 | 10 | 5246.1226
125M | 125.807 | 0.01 | 229.4388 | 10 | 9261.3777
150M | 149.562 | 0.01 | 362.8774 | 4.9972 | 10000
B VELOCITY REFERENCE LINES — Log-log anchor points
v [m/s] | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2)
0.2 | 0.01 | 39.3748 | 0.085481 | 1
0.3 | 0.01 | 207.3928 | 0.2274 | 1
0.4 | 0.01 | 670.015 | 0.45947 | 1
0.5 | 0.01 | 1748.294 | 0.76277 | 1
0.6 | 0.01 | 3823.996 | 1.1652 | 1
0.8 | 0.01085 | 10000 | 2.4177 | 1
1 | 0.019617 | 10000 | 4.1415 | 1
1.5 | 0.051835 | 10000 | 10 | 1.2357
2 | 0.10804 | 10000 | 10 | 3.9622
3 | 0.27379 | 10000 | 10 | 22.7505
5 | 0.92581 | 10000 | 10 | 189.8465
C EQUIVALENT LENGTHS [m] — 局部抵抗の相当長
DN_mm | elbow_90° | elbow_45° | tee_straight
10 | 0.2 | 0.2 | 0.2
15 | 0.3 | 0.18 | 0.09
20 | 0.38 | 0.23 | 0.12
25 | 0.45 | 0.3 | 0.14
32 | 0.61 | 0.36 | 0.18
40 | 0.76 | 0.45 | 0.24
50 | 1.06 | 0.61 | 0.3
65 | 1.21 | 0.76 | 0.39
80 | 1.52 | 0.91 | 0.45
Note: 消火設備の配管には適用しない。
Interpolation: m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)) b=log10(y1)−m·log10(x1) → Q=10^(m·log10(i)+b) ¦ i=10^((log10(Q)−b)/m)

## sgp
図7-5 鋼管（配管用炭素鋼鋼管）流量線図
Carbon steel pipe (JIS G 3452 SGP)
Formula | Hazen-Williams (HW)
C | 100
DN suffix | A
i range [kPa/m] | 0.01 – 10
Q range [L/min] | 1 – 10000
A PIPE SIZES — Log-log anchor points (x=i [kPa/m], y=Q [L/min])
DN | id_mm | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2) | note
15 A | 16.175 | 0.014781 | 1 | 10 | 31.9987
20 A | 21.787 | 0.01 | 1.7114 | 10 | 72.5487
25 A | 27.772 | 0.01 | 3.3468 | 10 | 132.9534
32 A | 36.16 | 0.01 | 6.6691 | 10 | 267.4128
40 A | 41.974 | 0.01 | 9.5587 | 10 | 408.8127
50 A | 53.223 | 0.01 | 18.1144 | 10 | 752.1436
65 A | 67.953 | 0.01 | 34.6472 | 10 | 1421.6385
80 A | 81.098 | 0.01 | 52.489 | 10 | 2377.405
90 A | 93.921 | 0.01 | 78.7877 | 10 | 3429.5962
100 A | 105.815 | 0.01 | 111.6074 | 10 | 4533.805
125 A | 133.072 | 0.01 | 195.1623 | 10 | 8653.6723
150 A | 158.55 | 0.01 | 308.8682 | 5.5524 | 10000
175 A | 181.62 | 0.01 | 439.2831 | 2.8391 | 10000
200 A | 206.664 | 0.01 | 653.127 | 1.6803 | 10000
225 A | 231.604 | 0.01 | 865.3403 | 0.9323 | 10000
250 A | 255.993 | 0.01 | 1096.2851 | 0.5451 | 10000
300 A | 307.768 | 0.01 | 1818.2914 | 0.2312 | 10000
350 A | 342.838 | 0.01 | 2382.2229 | 0.1333 | 10000
B VELOCITY REFERENCE LINES — Log-log anchor points
v [m/s] | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2)
0.2 | 0.01 | 95.5934 | 0.13785 | 1
0.3 | 0.01 | 518.4469 | 0.37851 | 1
0.4 | 0.01 | 1637.838 | 0.74896 | 1
0.5 | 0.01 | 4143.554 | 1.3383 | 1
0.6 | 0.01 | 8677.138 | 2.1489 | 1
0.8 | 0.019328 | 10000 | 4.186 | 1
1 | 0.032216 | 10000 | 7.2732 | 1
1.5 | 0.08907 | 10000 | 10 | 3.3934
2 | 0.17176 | 10000 | 10 | 10.5934
3 | 0.48977 | 10000 | 10 | 58.8663
5 | 1.6777 | 10000 | 10 | 487.5791
C EQUIVALENT LENGTHS [m] — 局部抵抗の相当長
DN_mm | elbow_90° | elbow_45° | tee_branch | tee_straight | gate_valve | globe_valve | angle_valve | check_swing | check_shock | Y_strainer
15 | 0.6 | 0.36 | 0.9 | 0.18 | 0.12 | 4.5 | 2.4 | 1.2 | — | 1.38
20 | 0.75 | 0.45 | 1.2 | 0.24 | 0.15 | 6 | 3.6 | 1.6 | — | 2.18
25 | 0.9 | 0.54 | 1.5 | 0.27 | 0.18 | 7.5 | 4.5 | 2 | — | 3
32 | 1.2 | 0.72 | 1.8 | 0.36 | 0.24 | 10.5 | 5.4 | 2.5 | — | 4.62
40 | 1.5 | 0.9 | 2.1 | 0.45 | 0.3 | 13.5 | 6.6 | 3.1 | — | 5.47
50 | 2.1 | 1.2 | 3 | 0.6 | 0.39 | 16.5 | 8.4 | 4 | 9.3 | 8
65 | 2.4 | 1.5 | 3.6 | 0.75 | 0.48 | 19.5 | 10.2 | 4.6 | 9.8 | 11.45
80 | 3 | 1.8 | 4.5 | 0.9 | 0.63 | 24 | 12 | 5.7 | 9 | 14.11
100 | 4.2 | 2.4 | 6.3 | 1.2 | 0.81 | 37.5 | 16.5 | 7.6 | 10.6 | 21.62
125 | 5.1 | 3 | 7.5 | 1.5 | 0.99 | 42 | 21 | 10 | 11.9 | 31.57
150 | 6 | 3.6 | 9 | 1.8 | 1.2 | 49.5 | 24 | 12 | 9.7 | 41.17
200 | 6.5 | 3.7 | 14 | 4 | 1.4 | 70 | 33 | 15 | 13.3 | 54.83
250 | 8 | 4.2 | 20 | 5 | 1.7 | 90 | 43 | 19 | 13.2 | 70.37
Note: 消火設備には適用しない。フート弁はアングル弁と同じ。ストレーナーはスクリーン7メッシュ程度。
Interpolation: m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)) b=log10(y1)−m·log10(x1) → Q=10^(m·log10(i)+b) ¦ i=10^((log10(Q)−b)/m)

## sus
図7-6 ステンレス鋼管（一般配管用）流量線図
Stainless steel pipe (JIS G 3448)
Formula | Hazen-Williams (HW)
C | 140
DN suffix | Su
i range [kPa/m] | 0.01 – 10
Q range [L/min] | 1 – 10000
A PIPE SIZES — Log-log anchor points (x=i [kPa/m], y=Q [L/min])
DN | id_mm | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2) | note
10 Su | 11.3 | — | — | — | — | formula only (use id_mm with HW)
13 Su | 14.54 | 0.01354 | 1 | 10 | 34.14
20 Su | 20.56 | 0.01 | 2.0934 | 10 | 85.722
25 Su | 26.9 | 0.01 | 4.2785 | 10 | 172.263
30 Su | 32.11 | 0.01 | 6.9427 | 10 | 269.297
40 Su | 40.78 | 0.01 | 12.7218 | 10 | 516.891
50 Su | 46.98 | 0.01 | 18.3245 | 10 | 755.753
60 Su | 58.47 | 0.01 | 32.5837 | 10 | 1343.921
75 Su | 74.2 | 0.01 | 62.3772 | 10 | 2456.675
80 Su | 86.68 | 0.01 | 90.3744 | 10 | 3843.717
100 Su | 112.12 | 0.01 | 182.702 | 10 | 7358.302
125 Su | 137.08 | 0.01 | 312.825 | 6.745 | 10000
150 Su | 160.81 | 0.01 | 478.306 | 3.127 | 10000
200 Su | 212.14 | 0.01 | 985.136 | 0.802 | 10000
250 Su | 264.5 | 0.01 | 1714.832 | 0.261 | 10000
300 Su | 318.38 | 0.01 | 2795.367 | 0.106 | 10000
B VELOCITY REFERENCE LINES — Log-log anchor points
v [m/s] | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2)
0.2 | 0.01 | 33.422 | 0.07647 | 1
0.3 | 0.01 | 179.068 | 0.20463 | 1
0.4 | 0.01 | 586.07 | 0.40981 | 1
0.5 | 0.01 | 1546.72 | 0.69975 | 1
0.6 | 0.01 | 3335.48 | 1.0877 | 1
0.8 | 0.01021 | 10000 | 2.2538 | 1
1 | 0.01796 | 10000 | 3.8391 | 1
1.5 | 0.04682 | 10000 | 10 | 1.044
2 | 0.09443 | 10000 | 10 | 3.509
3 | 0.25192 | 10000 | 10 | 19.545
5 | 0.86567 | 10000 | 10 | 160.611
C EQUIVALENT LENGTHS [m] — 局部抵抗の相当長
DN_mm | elbow_90° | elbow_45° | tee_branch | tee_straight | gate_valve*1 | globe_valve*2 | angle+check_swing | socket
13 | 0.3 | 0.18 | 0.45 | 0.09 | 0.06 | 2.27 | 2.4 | 0.09
20 | 0.38 | 0.23 | 0.61 | 0.12 | 0.08 | 3.03 | 3.6 | 0.12
25 | 0.45 | 0.3 | 0.76 | 0.14 | 0.09 | 3.79 | 4.5 | 0.14
40 | 0.61 | 0.36 | 0.91 | 0.18 | 0.12 | 5.45 | 5.4 | 0.18
50 | 0.76 | 0.45 | 1.06 | 0.24 | 0.15 | 6.97 | 6.8 | 0.24
60 | 1.06 | 0.61 | 1.52 | 0.3 | 0.21 | 8.48 | 8.4 | 0.3
75 | 1.21 | 0.76 | 1.82 | 0.39 | 0.24 | 10 | 10.2 | 0.39
80 | 1.52 | 0.91 | 2.27 | 0.45 | 0.3 | 12.12 | 12 | 0.45
100 | 2.12 | 1.21 | 3.18 | 0.61 | 0.42 | 19.09 | 16.5 | 0.61
125 | 2.73 | 1.52 | 3.94 | 0.76 | 0.52 | 21.21 | 21 | 0.76
150 | 3.03 | 1.82 | 4.55 | 0.91 | 0.61 | 25.45 | 21 | 0.91
Note: 消火設備には適用しない。*1 青銅鋳物製。*2 50A以下青銅鋳物製、65A以上鋳鉄製。
Interpolation: m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)) b=log10(y1)−m·log10(x1) → Q=10^(m·log10(i)+b) ¦ i=10^((log10(Q)−b)/m)

## hsgpw
図7-7 耐熱性硬質塩化ビニルライニング鋼管流量線図
Heat-resistant PVC-lined steel pipe (JIS G 3442 hot water)
Formula | Hazen-Williams (HW)
C | 130
DN suffix | A
i range [kPa/m] | 0.01 – 10
Q range [L/min] | 1 – 10000
A PIPE SIZES — Log-log anchor points (x=i [kPa/m], y=Q [L/min])
DN | id_mm | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2) | note
15 A | 11.282 | 0.056906 | 1 | 10 | 16.8372
20 A | 16.86 | 0.01 | 1.1287 | 10 | 48.2607
25 A | 22.889 | 0.01 | 2.5529 | 10 | 106.5511
32 A | 30.228 | 0.01 | 5.3199 | 10 | 220.7964
40 A | 36.159 | 0.01 | 8.5733 | 10 | 351.5888
50 A | 47.643 | 0.01 | 17.7509 | 10 | 724.4215
65 A | 61.129 | 0.01 | 34.283 | 10 | 1391.6016
80 A | 73.896 | 0.01 | 55.5807 | 10 | 2327.8355
100 A | 99.258 | 0.01 | 120.5873 | 10 | 5065.5411
B VELOCITY REFERENCE LINES — Log-log anchor points
v [m/s] | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2)
0.2 | 0.01 | 41.8865 | 0.089482 | 1
0.3 | 0.01 | 212.9278 | 0.24364 | 1
0.4 | 0.01 | 722.367 | 0.50036 | 1
0.5 | 0.01 | 1790.498 | 0.8283 | 1
0.6 | 0.01 | 3877.77 | 1.3525 | 1
0.8 | 0.010902 | 10000 | 2.7256 | 1
1 | 0.019468 | 10000 | 4.4758 | 1
1.5 | 0.051604 | 10000 | 10 | 1.4337
2 | 0.11173 | 10000 | 10 | 4.3675
3 | 0.28908 | 10000 | 10 | 23.3225
5 | 1.0178 | 10000 | 10 | 196.7048
C EQUIVALENT LENGTHS [m] — 局部抵抗の相当長
DN_mm | elbow_90° | elbow_45° | tee_branch | tee_straight | gate_valve | globe_valve | angle_valve | check_swing | check_shock | Y_strainer
15 | *1.6 | *0.8 | *1.8 | *0.6 | *14.2 | 4.5 | 2.4 | *14.2 | — | *4.25
20 | *1.8 | *0.9 | *2.0 | *0.6 | *4.2 | 6 | 3.6 | *4.9 | — | *3.22
25 | *2.0 | *1.0 | *2.2 | *0.5 | *2.4 | 7.5 | 4.5 | *2.9 | — | *3.38
32 | *2.2 | *1.0 | *2.5 | *0.5 | *3.2 | 10.5 | 5.4 | *3.8 | — | *5.52
40 | *2.5 | *1.2 | *2.8 | *0.6 | *2.5 | 13.5 | 6.6 | *2.7 | — | *6.25
50 | *2.8 | *1.3 | *3.1 | *0.6 | *2.1 | 16.5 | 8.4 | *5.0 | 9.3 | *6.64
65 | *2.8 | *1.5 | *4.0 | *0.7 | 0.48 | 19.5 | 10.2 | 4.6 | 9.8 | 11.45
80 | *3.3 | *1.8 | *5.0 | *0.8 | 0.63 | 24 | 12 | 5.7 | 9 | 14.11
100 | *4.2 | *2.3 | *6.8 | *1.0 | 0.81 | 37.5 | 16.5 | 7.6 | 10.6 | 21.62
Note: * = 管端防食機構付き。フート弁はアングル弁と同じ。ストレーナーはスクリーン7メッシュ程度。
Interpolation: m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)) b=log10(y1)−m·log10(x1) → Q=10^(m·log10(i)+b) ¦ i=10^((log10(Q)−b)/m)

## poly
図7-8 ポリエチレン管流量線図
Polyethylene pipe (JIS K 6762) — TW formula C=215
Formula | TW
C | 215
DN suffix
i range [kPa/m] | 0.1 – 5
Q range [L/min] | 10 – 400
A PIPE SIZES — Log-log anchor points (x=i [kPa/m], y=Q [L/min])
DN | id_mm | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2) | note
13 | 12.371 | 1.0296 | 10 | 5 | 24.5583
20 | 16.255 | 0.28016 | 10 | 5 | 51.1158
25 | 20.68 | 0.1 | 10.835 | 5 | 95.9641
30 | 27.189 | 0.1 | 22.357 | 5 | 196.2221
40 | 30.89 | 0.1 | 30.901 | 5 | 277.6959
50 | 39.13 | 0.1 | 57.955 | 3.1464 | 400
B VELOCITY REFERENCE LINES — Log-log anchor points
v [m/s] | x1 (i start) | y1 (Q at x1) | x2 (i end) | y2 (Q at x2)
0.6 | 0.1 | 51.471 | 0.29533 | 10
0.8 | 0.1 | 140.612 | 0.61078 | 10
1 | 0.1 | 316.109 | 1.0473 | 10
1.5 | 0.23377 | 400 | 2.7195 | 10
2 | 0.48819 | 400 | 5 | 11.2193
3 | 1.331 | 400 | 5 | 51.5141
4 | 2.6404 | 400 | 5 | 148.1843
Note: 表7-10 管の均等表（同一流量・同一圧損となる管径の比率）— see JSON sheet for full subtables
Interpolation: m=(log10(y2)−log10(y1))/(log10(x2)−log10(x1)) b=log10(y1)−m·log10(x1) → Q=10^(m·log10(i)+b) ¦ i=10^((log10(Q)−b)/m)

## JSON
Full JSON reference — copy cell B2 content into your software
JSON blob → | { "_meta": { "formula_hw": "Q=4.87*C*d^2.63*i^0.54*1000", "units": { "Q": "L/min", "i": "kPa/m", "id_mm": "mm", "v": "m/s", "eq_len": "m" }, "anchor_note": "Each pipe line stored as two log-log digitised endpoints (x1,y1)→(x2,y2). Interpolate: log10(Q)=m*log10(i)+b", "interp_Q": "Q=10^(m*log10(i)+b)", "interp_i": "i=10^((log10(Q)-b)/m)", "velocity": "v=(Q/60/1000)/(pi/4*(id_mm/1000)^2)", "eff_id": "avg((y1/(4870*C*x1^0.54))^(1/2.63)*1000,(y2/(4870*C*x2^0.54))^(1/2.63)*1000)" }, "pipes": { "sgpw": { "title": "硬質塩化ビニルライニング鋼管流量線図", "title_en": "Hard PVC-lined steel pipe (JIS G 3442 SGPW)", "figNo": "図7-2", "C": 130, "suffix": "A", "Xmin": 0.01, "Xmax": 10, "Ymin": 1, "Ymax": 10000, "sizes": [ { "DN": 15, "id_mm": 13.263, "x1": 0.023429, "y1": 1, "x2": 10, "y2": 24.4057 }, { "DN": 20, "id_mm": 18.911, "x1": 0.01, "y1": 1.5994, "x2": 10, "y2": 62.2709 }, { "DN": 25, "id_mm": 25.128, "x1": 0.01, "y1": 3.2787, "x2": 10, "y2": 135.5285 }, { "DN": 32, "id_mm": 33.31, "x1": 0.01, "y1": 7.0128, "x2": 10, "y2": 279.0647 }, { "DN": 40, "id_mm": 39.026, "x1": 0.01, "y1": 10.569, "x2": 10, "y2": 425.9633 }, { "DN": 50, "id_mm": 50.644, "x1": 0.01, "y1": 20.5322, "x2": 10, "y2": 863.6182 }, { "DN": 65, "id_mm": 65.843, "x1": 0.01, "y1": 40.8699, "x2": 10, "y2": 1725.4212 }, { "DN": 80, "id_mm": 77.834, "x1": 0.01, "y1": 64.9727, "x2": 10, "y2": 2616.5304 }, { "DN": 100, "id_mm": 102.428, "x1": 0.01, "y1": 131.0725, "x2": 10, "y2": 5498.3146 }, { "DN": 125, "id_mm": 127.267, "x1": 0.01, "y1": 232.0, "x2": 10, "y2": 9733.2501 }, { "DN": 150, "id_mm": 151.92, "x1": 0.01, "y1": 364.7822, "x2": 4.3325, "y2": 10000 }, { "DN": 200, "id_mm": 201.539, "x1": 0.01, "y1": 765.5682, "x2": 1.0898, "y2": 10000 }, { "DN": 250, "id_mm": 250.625, "x1": 0.01, "y1": 1404.7116, "x2": 0.4012, "y2": 10000 }, { "DN": 300, "id_mm": 299.714, "x1": 0.01, "y1": 2180.454, "x2": 0.1586, "y2": 10000 }, { "DN": 350, "id_mm": 335.318, "x1": 0.01, "y1": 2934.3961, "x2": 0.0921, "y2": 10000 } ], "vel": [ { "v": 0.2, "x1": 0.01, "y1": 39.5044, "x2": 0.086747, "y2": 1 }, { "v": 0.3, "x1": 0.01, "y1": 218.5244, "x2": 0.231318, "y2": 1 }, { "v": 0.4, "x1": 0.01, "y1": 760.6724, "x2": 0.459812, "y2": 1 }, { "v": 0.6, "x1": 0.01, "y1": 4055.063, "x2": 1.227685, "y2": 1 }, { "v": 0.8, "x1": 0.011917, "y1": 10000, "x2": 2.366904, "y2": 1 }, { "v": 1.0, "x1": 0.020604, "y1": 10000, "x2": 4.092374, "y2": 1 }, { "v": 1.5, "x1": 0.052234, "y1": 10000, "x2": 10, "y2": 1.285139 }, { "v": 2.0, "x1": 0.107033, "y1": 10000, "x2": 10, "y2": 4.114542 }, { "v": 3.0, "x1": 0.291219, "y1": 10000, "x2": 10, "y2": 21.971581 }, { "v": 5.0, "x1": 1.009213, "y1": 10000, "x2": 10, "y2": 188.09553 } ], "eq_cols": [ "DN_mm", "elbow_90°", "elbow_45°", "tee_branch", "tee_straight", "gate_valve", "globe_valve", "angle_valve", "check_swing", "check_shock", "Y_strainer", "socket" ], "eq_rows": [ [ 15, "*3.0", "*2.3", "*3.8", "*1.2", "*3.50", 4.5, 2.4, "*5.5", "", "*3.34", "*1.0" ], [ 20, "*3.1", "*2.2", "*3.8", "*1.6", "*2.30", 6.0, 3.6, "*2.7", "", "*4.37", "*0.7" ], [ 25, "*3.2", "*1.8", "*3.3", "*1.2", "*1.70", 7.5, 4.5, "*2.9", "", "*5.85", "*0.5" ], [ 32, "*3.6", "*2.3", "*4.0", "*1.4", "*1.30", 10.5, 5.4, "*3.2", "", "*8.51", "*0.7" ], [ 40, "*3.3", "*1.9", "*3.6", "*0.9", "*1.70", 13.5, 6.6, "*2.6", "", "*8.25", "*0.6" ], [ 50, "*3.3", "*1.9", "*3.5", "*0.9", "*1.90", 16.5, 8.4, "*3.7", 9.3, "*9.79", "*0.4" ], [ 65, "*4.4", "*2.4", "*4.4", "*1.1", 0.48, 19.5, 10.2, 4.6, 9.8, 11.45, "*0.4" ], [ 80, "*4.6", "*2.4", "*4.9", "*1.3", 0.63, 24.0, 12.0, 5.7, 9.0, 14.11, "*0.4" ], [ 100, 4.2, 2.4, 6.3, 1.2, 0.81, 37.5, 16.5, 7.6, 10.6, 21.62, "" ], [ 125, 5.1, 3.0, 7.5, 1.5, 0.99, 42.0, 21.0, 10.0, 11.9, 31.57, "" ], [ 150, 6.0, 3.6, 9.0, 1.8, 1.2, 49.5, 24.0, 12.0, 9.7, 41.17, "" ], [ 200, 6.5, 3.7, 14.0, 4.0, 1.4, 70.0, 33.0, 15.0, 13.3, 54.83, "" ], [ 250, 8.0, 4.2, 20.0, 5.0, 1.7, 90.0, 43.0, 19.0, 13.2, 70.37, "" ] ], "eq_note": "* = 管端防食機構付き。フート弁はアングル弁と同じ。ストレーナーはスクリーン7メッシュ程度。" }, "vpvc": { "title": "硬質ポリ塩化ビニル管流量線図", "title_en": "Rigid PVC pipe (JIS K 6741 VP/HIVP)", "figNo": "図7-3", "C": 130, "suffix": "", "Xmin": 0.01, "Xmax": 10, "Ymin": 1, "Ymax": 10000, "sizes": [ { "DN": 13, "id_mm": 13.785, "x1": 0.021813, "y1": 1, "x2": 10, "y2": 28.7766 }, { "DN": 16, "id_mm": 16.745, "x1": 0.01, "y1": 1.1242, "x2": 10, "y2": 46.7425 }, { "DN": 20, "id_mm": 20.948, "x1": 0.01, "y1": 2.0167, "x2": 10, "y2": 84.6348 }, { "DN": 25, "id_mm": 25.855, "x1": 0.01, "y1": 3.5508, "x2": 10, "y2": 145.4083 }, { "DN": 30, "id_mm": 31.935, "x1": 0.01, "y1": 6.1639, "x2": 10, "y2": 254.4254 }, { "DN": 40, "id_mm": 40.941, "x1": 0.01, "y1": 11.8681, "x2": 10, "y2": 488.1309 }, { "DN": 50, "id_mm": 52.106, "x1": 0.01, "y1": 22.3254, "x2": 10, "y2": 922.5302 }, { "DN": 65, "id_mm": 68.523, "x1": 0.01, "y1": 44.0101, "x2": 10, "y2": 1975.4219 }, { "DN": 75, "id_mm": 78.339, "x1": 0.01, "y1": 63.9425, "x2": 10, "y2": 2750.7281 }, { "DN": 100, "id_mm": 101.074, "x1": 0.01, "y1": 126.6856, "x2": 10, "y2": 5304.1643 }, { "DN": 125, "id_mm": 125.776, "x1": 0.01, "y1": 221.7195, "x2": 10, "y2": 9571.2948 }, { "DN": 150, "id_mm": 148.228, "x1": 0.01, "y1": 340.8615, "x2": 4.8562, "y2": 10000 } ], "vel": [ { "v": 0.2, "x1": 0.01, "y1": 39.1558, "x2": 0.088642, "y2": 1 }, { "v": 0.3, "x1": 0.01, "y1": 209.8414, "x2": 0.236039, "y2": 1 }, { "v": 0.4, "x1": 0.01, "y1": 686.0807, "x2": 0.482251, "y2": 1 }, { "v": 0.5, "x1": 0.01, "y1": 1665.387, "x2": 0.811568, "y2": 1 }, { "v": 0.6, "x1": 0.01, "y1": 3421.851, "x2": 1.300716, "y2": 1 }, { "v": 0.8, "x1": 0.011206, "y1": 10000, "x2": 2.599362, "y2": 1 }, { "v": 1.0, "x1": 0.019441, "y1": 10000, "x2": 4.575835, "y2": 1 }, { "v": 1.5, "x1": 0.051531, "y1": 10000, "x2": 10, "y2": 1.42086 }, { "v": 2.0, "x1": 0.112337, "y1": 10000, "x2": 10, "y2": 4.359238 }, { "v": 3.0, "x1": 0.291141, "y1": 10000, "x2": 10, "y2": 24.968009 }, { "v": 5.0, "x1": 1.036486, "y1": 10000, "x2": 10, "y2": 202.873818 } ], "eq_cols": [ "DN_mm", "elbow_90°", "bend_90°", "elbow_45°", "tee_reducer_socket" ], "eq_rows": [ [ 13, 0.5, "", "", "" ], [ 16, 0.5, "", "", "" ], [ 20, 0.5, "", "", "" ], [ 25, 0.5, "", "", "" ], [ 30, 0.8, "", "", 1.0 ], [ 40, 0.8, "", "", 1.0 ], [ 50, 1.2, "", "", 1.5 ], [ 75, "", 1.5, 0.8, 2.0 ], [ 100, "", 2.0, 1.0, 3.0 ], [ 125, "", 3.0, 1.5, 5.0 ] ], "eq_note": "チー及び径違いソケットは設置された側の呼び径とする。チー分流は90°エルボ＋チー直流。" }, "copper": { "title": "銅管流量線図", "title_en": "Copper pipe (JIS H 3300 L/M type)", "figNo": "図7-4", "C": 130, "suffix": "", "Xmin": 0.01, "Xmax": 10, "Ymin": 1, "Ymax": 10000, "sizes": [ { "DN": "10L", "id_mm": 11.049, "x1": 0.061965, "y1": 1, "x2": 10, "y2": 15.7956 }, { "DN": "10M", "id_mm": 11.59, "x1": 0.049107, "y1": 1, "x2": 10, "y2": 17.9145 }, { "DN": "15L", "id_mm": 14.046, "x1": 0.01942, "y1": 1, "x2": 10, "y2": 29.8363 }, { "DN": "15M", "id_mm": 14.664, "x1": 0.014999, "y1": 1, "x2": 10, "y2": 32.5447 }, { "DN": "20L", "id_mm": 19.989, "x1": 0.01, "y1": 1.7595, "x2": 10, "y2": 75.802 }, { "DN": "20M", "id_mm": 20.759, "x1": 0.01, "y1": 1.9742, "x2": 10, "y2": 82.4236 }, { "DN": "25L", "id_mm": 26.037, "x1": 0.01, "y1": 3.6244, "x2": 10, "y2": 147.8219 }, { "DN": "25M", "id_mm": 27.268, "x1": 0.01, "y1": 4.0815, "x2": 10, "y2": 167.3703 }, { "DN": "32M", "id_mm": 32.893, "x1": 0.01, "y1": 6.629, "x2": 10, "y2": 276.3314 }, { "DN": "40M", "id_mm": 39.116, "x1": 0.01, "y1": 10.5715, "x2": 10, "y2": 431.0667 }, { "DN": "50M", "id_mm": 51.382, "x1": 0.01, "y1": 21.504, "x2": 10, "y2": 889.7842 }, { "DN": "65M", "id_mm": 63.611, "x1": 0.01, "y1": 36.8398, "x2": 10, "y2": 1596.3719 }, { "DN": "80M", "id_mm": 76.079, "x1": 0.01, "y1": 59.7493, "x2": 10, "y2": 2523.8251 }, { "DN": "100M", "id_mm": 100.803, "x1": 0.01, "y1": 126.2924, "x2": 10, "y2": 5246.1226 }, { "DN": "125M", "id_mm": 125.807, "x1": 0.01, "y1": 229.4388, "x2": 10, "y2": 9261.3777 }, { "DN": "150M", "id_mm": 149.562, "x1": 0.01, "y1": 362.8774, "x2": 4.9972, "y2": 10000 } ], "vel": [ { "v": 0.2, "x1": 0.01, "y1": 39.3748, "x2": 0.085481, "y2": 1 }, { "v": 0.3, "x1": 0.01, "y1": 207.3928, "x2": 0.2274, "y2": 1 }, { "v": 0.4, "x1": 0.01, "y1": 670.015, "x2": 0.459474, "y2": 1 }, { "v": 0.5, "x1": 0.01, "y1": 1748.294, "x2": 0.762769, "y2": 1 }, { "v": 0.6, "x1": 0.01, "y1": 3823.996, "x2": 1.165171, "y2": 1 }, { "v": 0.8, "x1": 0.01085, "y1": 10000, "x2": 2.417684, "y2": 1 }, { "v": 1.0, "x1": 0.019617, "y1": 10000, "x2": 4.141502, "y2": 1 }, { "v": 1.5, "x1": 0.051835, "y1": 10000, "x2": 10, "y2": 1.23573 }, { "v": 2.0, "x1": 0.108038, "y1": 10000, "x2": 10, "y2": 3.962172 }, { "v": 3.0, "x1": 0.27379, "y1": 10000, "x2": 10, "y2": 22.750542 }, { "v": 5.0, "x1": 0.925808, "y1": 10000, "x2": 10, "y2": 189.846506 } ], "eq_cols": [ "DN_mm", "elbow_90°", "elbow_45°", "tee_straight" ], "eq_rows": [ [ 10, 0.2, 0.2, 0.2 ], [ 15, 0.3, 0.18, 0.09 ], [ 20, 0.38, 0.23, 0.12 ], [ 25, 0.45, 0.3, 0.14 ], [ 32, 0.61, 0.36, 0.18 ], [ 40, 0.76, 0.45, 0.24 ], [ 50, 1.06, 0.61, 0.3 ], [ 65, 1.21, 0.76, 0.39 ], [ 80, 1.52, 0.91, 0.45 ] ], "eq_note": "消火設備の配管には適用しない。" }, "sgp": { "title": "鋼管（配管用炭素鋼鋼管）流量線図", "title_en": "Carbon steel pipe (JIS G 3452 SGP)", "figNo": "図7-5", "C": 100, "suffix": "A", "Xmin": 0.01, "Xmax": 10, "Ymin": 1, "Ymax": 10000, "sizes": [ { "DN": 15, "id_mm": 16.175, "x1": 0.014781, "y1": 1, "x2": 10, "y2": 31.9987 }, { "DN": 20, "id_mm": 21.787, "x1": 0.01, "y1": 1.7114, "x2": 10, "y2": 72.5487 }, { "DN": 25, "id_mm": 27.772, "x1": 0.01, "y1": 3.3468, "x2": 10, "y2": 132.9534 }, { "DN": 32, "id_mm": 36.16, "x1": 0.01, "y1": 6.6691, "x2": 10, "y2": 267.4128 }, { "DN": 40, "id_mm": 41.974, "x1": 0.01, "y1": 9.5587, "x2": 10, "y2": 408.8127 }, { "DN": 50, "id_mm": 53.223, "x1": 0.01, "y1": 18.1144, "x2": 10, "y2": 752.1436 }, { "DN": 65, "id_mm": 67.953, "x1": 0.01, "y1": 34.6472, "x2": 10, "y2": 1421.6385 }, { "DN": 80, "id_mm": 81.098, "x1": 0.01, "y1": 52.489, "x2": 10, "y2": 2377.405 }, { "DN": 90, "id_mm": 93.921, "x1": 0.01, "y1": 78.7877, "x2": 10, "y2": 3429.5962 }, { "DN": 100, "id_mm": 105.815, "x1": 0.01, "y1": 111.6074, "x2": 10, "y2": 4533.805 }, { "DN": 125, "id_mm": 133.072, "x1": 0.01, "y1": 195.1623, "x2": 10, "y2": 8653.6723 }, { "DN": 150, "id_mm": 158.55, "x1": 0.01, "y1": 308.8682, "x2": 5.5524, "y2": 10000 }, { "DN": 175, "id_mm": 181.62, "x1": 0.01, "y1": 439.2831, "x2": 2.8391, "y2": 10000 }, { "DN": 200, "id_mm": 206.664, "x1": 0.01, "y1": 653.127, "x2": 1.6803, "y2": 10000 }, { "DN": 225, "id_mm": 231.604, "x1": 0.01, "y1": 865.3403, "x2": 0.9323, "y2": 10000 }, { "DN": 250, "id_mm": 255.993, "x1": 0.01, "y1": 1096.2851, "x2": 0.5451, "y2": 10000 }, { "DN": 300, "id_mm": 307.768, "x1": 0.01, "y1": 1818.2914, "x2": 0.2312, "y2": 10000 }, { "DN": 350, "id_mm": 342.838, "x1": 0.01, "y1": 2382.2229, "x2": 0.1333, "y2": 10000 } ], "vel": [ { "v": 0.2, "x1": 0.01, "y1": 95.5934, "x2": 0.137854, "y2": 1 }, { "v": 0.3, "x1": 0.01, "y1": 518.4469, "x2": 0.378514, "y2": 1 }, { "v": 0.4, "x1": 0.01, "y1": 1637.838, "x2": 0.748959, "y2": 1 }, { "v": 0.5, "x1": 0.01, "y1": 4143.554, "x2": 1.338312, "y2": 1 }, { "v": 0.6, "x1": 0.01, "y1": 8677.138, "x2": 2.148948, "y2": 1 }, { "v": 0.8, "x1": 0.019328, "y1": 10000, "x2": 4.186021, "y2": 1 }, { "v": 1.0, "x1": 0.032216, "y1": 10000, "x2": 7.273231, "y2": 1 }, { "v": 1.5, "x1": 0.08907, "y1": 10000, "x2": 10, "y2": 3.39343 }, { "v": 2.0, "x1": 0.171762, "y1": 10000, "x2": 10, "y2": 10.593366 }, { "v": 3.0, "x1": 0.489768, "y1": 10000, "x2": 10, "y2": 58.866267 }, { "v": 5.0, "x1": 1.677748, "y1": 10000, "x2": 10, "y2": 487.579118 } ], "eq_cols": [ "DN_mm", "elbow_90°", "elbow_45°", "tee_branch", "tee_straight", "gate_valve", "globe_valve", "angle_valve", "check_swing", "check_shock", "Y_strainer" ], "eq_rows": [ [ 15, 0.6, 0.36, 0.9, 0.18, 0.12, 4.5, 2.4, 1.2, "", 1.38 ], [ 20, 0.75, 0.45, 1.2, 0.24, 0.15, 6.0, 3.6, 1.6, "", 2.18 ], [ 25, 0.9, 0.54, 1.5, 0.27, 0.18, 7.5, 4.5, 2.0, "", 3.0 ], [ 32, 1.2, 0.72, 1.8, 0.36, 0.24, 10.5, 5.4, 2.5, "", 4.62 ], [ 40, 1.5, 0.9, 2.1, 0.45, 0.3, 13.5, 6.6, 3.1, "", 5.47 ], [ 50, 2.1, 1.2, 3.0, 0.6, 0.39, 16.5, 8.4, 4.0, 9.3, 8.0 ], [ 65, 2.4, 1.5, 3.6, 0.75, 0.48, 19.5, 10.2, 4.6, 9.8, 11.45 ], [ 80, 3.0, 1.8, 4.5, 0.9, 0.63, 24.0, 12.0, 5.7, 9.0, 14.11 ], [ 100, 4.2, 2.4, 6.3, 1.2, 0.81, 37.5, 16.5, 7.6, 10.6, 21.62 ], [ 125, 5.1, 3.0, 7.5, 1.5, 0.99, 42.0, 21.0, 10.0, 11.9, 31.57 ], [ 150, 6.0, 3.6, 9.0, 1.8, 1.2, 49.5, 24.0, 12.0, 9.7, 41.17 ], [ 200, 6.5, 3.7, 14.0, 4.0, 1.4, 70.0, 33.0, 15.0, 13.3, 54.83 ], [ 250, 8.0, 4.2, 20.0, 5.0, 1.7, 90.0, 43.0, 19.0, 13.2, 70.37 ] ], "eq_note": "消火設備には適用しない。フート弁はアングル弁と同じ。ストレーナーはスクリーン7メッシュ程度。" }, "sus": { "title": "ステンレス鋼管（一般配管用）流量線図", "title_en": "Stainless steel pipe (JIS G 3448)", "figNo": "図7-6", "C": 140, "suffix": "Su", "Xmin": 0.01, "Xmax": 10, "Ymin": 1, "Ymax": 10000, "sizes": [ { "DN": 10, "id_mm": 11.3, "x1": null, "y1": null, "x2": null, "y2": null }, { "DN": 13, "id_mm": 14.54, "x1": 0.01354, "y1": 1, "x2": 10, "y2": 34.14 }, { "DN": 20, "id_mm": 20.56, "x1": 0.01, "y1": 2.0934, "x2": 10, "y2": 85.722 }, { "DN": 25, "id_mm": 26.9, "x1": 0.01, "y1": 4.2785, "x2": 10, "y2": 172.263 }, { "DN": 30, "id_mm": 32.11, "x1": 0.01, "y1": 6.9427, "x2": 10, "y2": 269.297 }, { "DN": 40, "id_mm": 40.78, "x1": 0.01, "y1": 12.7218, "x2": 10, "y2": 516.891 }, { "DN": 50, "id_mm": 46.98, "x1": 0.01, "y1": 18.3245, "x2": 10, "y2": 755.753 }, { "DN": 60, "id_mm": 58.47, "x1": 0.01, "y1": 32.5837, "x2": 10, "y2": 1343.921 }, { "DN": 75, "id_mm": 74.2, "x1": 0.01, "y1": 62.3772, "x2": 10, "y2": 2456.675 }, { "DN": 80, "id_mm": 86.68, "x1": 0.01, "y1": 90.3744, "x2": 10, "y2": 3843.717 }, { "DN": 100, "id_mm": 112.12, "x1": 0.01, "y1": 182.702, "x2": 10, "y2": 7358.302 }, { "DN": 125, "id_mm": 137.08, "x1": 0.01, "y1": 312.825, "x2": 6.745, "y2": 10000 }, { "DN": 150, "id_mm": 160.81, "x1": 0.01, "y1": 478.306, "x2": 3.127, "y2": 10000 }, { "DN": 200, "id_mm": 212.14, "x1": 0.01, "y1": 985.136, "x2": 0.802, "y2": 10000 }, { "DN": 250, "id_mm": 264.5, "x1": 0.01, "y1": 1714.832, "x2": 0.261, "y2": 10000 }, { "DN": 300, "id_mm": 318.38, "x1": 0.01, "y1": 2795.367, "x2": 0.106, "y2": 10000 } ], "vel": [ { "v": 0.2, "x1": 0.01, "y1": 33.422, "x2": 0.07647, "y2": 1 }, { "v": 0.3, "x1": 0.01, "y1": 179.068, "x2": 0.20463, "y2": 1 }, { "v": 0.4, "x1": 0.01, "y1": 586.07, "x2": 0.40981, "y2": 1 }, { "v": 0.5, "x1": 0.01, "y1": 1546.72, "x2": 0.69975, "y2": 1 }, { "v": 0.6, "x1": 0.01, "y1": 3335.48, "x2": 1.0877, "y2": 1 }, { "v": 0.8, "x1": 0.01021, "y1": 10000, "x2": 2.25377, "y2": 1 }, { "v": 1.0, "x1": 0.01796, "y1": 10000, "x2": 3.83909, "y2": 1 }, { "v": 1.5, "x1": 0.04682, "y1": 10000, "x2": 10, "y2": 1.044 }, { "v": 2.0, "x1": 0.09443, "y1": 10000, "x2": 10, "y2": 3.509 }, { "v": 3.0, "x1": 0.25192, "y1": 10000, "x2": 10, "y2": 19.545 }, { "v": 5.0, "x1": 0.86567, "y1": 10000, "x2": 10, "y2": 160.611 } ], "eq_cols": [ "DN_mm", "elbow_90°", "elbow_45°", "tee_branch", "tee_straight", "gate_valve*1", "globe_valve*2", "angle+check_swing", "socket" ], "eq_rows": [ [ 13, 0.3, 0.18, 0.45, 0.09, 0.06, 2.27, 2.4, 0.09 ], [ 20, 0.38, 0.23, 0.61, 0.12, 0.08, 3.03, 3.6, 0.12 ], [ 25, 0.45, 0.3, 0.76, 0.14, 0.09, 3.79, 4.5, 0.14 ], [ 40, 0.61, 0.36, 0.91, 0.18, 0.12, 5.45, 5.4, 0.18 ], [ 50, 0.76, 0.45, 1.06, 0.24, 0.15, 6.97, 6.8, 0.24 ], [ 60, 1.06, 0.61, 1.52, 0.3, 0.21, 8.48, 8.4, 0.3 ], [ 75, 1.21, 0.76, 1.82, 0.39, 0.24, 10.0, 10.2, 0.39 ], [ 80, 1.52, 0.91, 2.27, 0.45, 0.3, 12.12, 12.0, 0.45 ], [ 100, 2.12, 1.21, 3.18, 0.61, 0.42, 19.09, 16.5, 0.61 ], [ 125, 2.73, 1.52, 3.94, 0.76, 0.52, 21.21, 21.0, 0.76 ], [ 150, 3.03, 1.82, 4.55, 0.91, 0.61, 25.45, 21.0, 0.91 ] ], "eq_note": "消火設備には適用しない。*1 青銅鋳物製。*2 50A以下青銅鋳物製、65A以上鋳鉄製。" }, "hsgpw": { "title": "耐熱性硬質塩化ビニルライニング鋼管流量線図", "title_en": "Heat-resistant PVC-lined steel pipe (JIS G 3442 hot water)", "figNo": "図7-7", "C": 130, "suffix": "A", "Xmin": 0.01, "Xmax": 10, "Ymin": 1, "Ymax": 10000, "sizes": [ { "DN": 15, "id_mm": 11.282, "x1": 0.056906, "y1": 1, "x2": 10, "y2": 16.8372 }, { "DN": 20, "id_mm": 16.86, "x1": 0.01, "y1": 1.1287, "x2": 10, "y2": 48.2607 }, { "DN": 25, "id_mm": 22.889, "x1": 0.01, "y1": 2.5529, "x2": 10, "y2": 106.5511 }, { "DN": 32, "id_mm": 30.228, "x1": 0.01, "y1": 5.3199, "x2": 10, "y2": 220.7964 }, { "DN": 40, "id_mm": 36.159,
(Cell B2 contains the full JSON. Copy its value — it will not wrap in Excel but can be copied to a text file.)